## Design Guide
Anaerobic Baffled Reactor Sizing Worksheet
This is for demonstration only and not a substitution for actual engineering. Project proponents should always hire a skilled engineer for wastewater system design
|  | Maximum number of people served by project |  |  |  | 100 |  | (type the number of people in the box)
|  | Average daily flow rate per person per day |  |  |  | 150 | l/day | Note: Average is 150 liters per day.
*Increase to 300 liters/day for affluent communities
*Decrease to 100 liters/day for less affluent communities
*Insert your own figure based on local knowledge
|  | Waste Flow Rate |  |  |  | 0.85 | 85% | How much of the incoming water is converted to wastewater
*Use project specific information to adjust as needed
|  | Daily flow volume |  | 12750 | liters
|  | Storage Factor |  | 1.35 | * see note at bottom of page |  |  | NOTE: For sources with known flows, insert the flow in cubic meters/day in cell E18
|  | Adjusted flow volume |  | 17212.5 | liters
|  | Volume in cubic meters = |  | 17.2125 | cubic meters
Suggested Dimensions of ABR
Profile View of Anaerobic Baffled Reactor
[5 empty] | (grade) | [7 empty] | 0.6m
| Tank depth = |  | 1.8
| Tank width = |  | 2.0744 | m
| Tank length = |  | 4.6052 | m
|  |  | 17.1953 | cu. M
(liquid level)
0.60788
NOTES:
1.6
| 1. All dimensions are in meters | [12 empty] | 1.5 | 1.8
| 2. Drawing is not to scale | [8 empty] | 1.25
3. These are suggested values only
4. Always confirm calculations with
| a sanitary engineer | [5 empty] | 1.5351
4.6052
Construction Notes:
End View of ABR Tank
1. Use poured in place concrete or concrete hollow blocks filled with grout
2. If hollow blocks, coat inside of tank with waterproofing material
3. Pipes should be 10 cm in diameter PVC or equivalent
4. Do a leak test before backfilling around tank. Follow these procedures:
a. Fill tank with water to halfway point. Look around outside of tank
for visible leaks. Check if water level drops. If no
|  |  | visible leaks and water level does not drop, fill in around | [5 empty] | 1.8
|  |  | outside of tank with soil and compact | [8 empty] | 1.5
b. Fill tank with water so that it is full. Repeat inspection as in a. above
c. Perform final leak test. With tank full, allow to sit for 24 hours.
Refill tank if needed. Then observe tank for 1 hour.
If water level drops more than 0.5 cm, tank has a leak that
| See "Details" sheet for location and dimensions of pipes and manholes |  | must be repaired.
2.0744
* Note - use this worksheet for between 30 to 250 people served
- For larger flows, more compartments are required. Consider 7 or 9 chambers
The length of the chamber should never be more then half the height
- For smaller flows, consider using a standard 2 or 3 compartment septic tank sized at 2 times the daily flow
NOTE: Residential wastewater considered low strength - this model uses a 1.35 storage factor for low strength waste
|  | - for medium strength wastewater - hospitals or public markets, use a storage factor of 1.8 to 2.4 | [8 empty] | to adjust, modify cell 9F
|  | - for high strength wastewater from food processing, animal waste, use a storage factor of 2.5 to 3.5 | [8 empty] | to adjust, modify cell 9F
This is not a substitute for actual engineering, but only a guide to help determine approximate size of the system. Always hire a competent engineer for wastewater projects.

## Details
Details
| ABR Profile View |  | Sample design for | 17.2125 | cubic meters per day
0
|  | 1.5351 |  |  | 0.76753
4.6052
ABR Plan View
0